## Table 1
Electrical Inspection Checklists
Checklist 1: General Safety Checklist for Electrical Inspections
✔ | Item | Basic Hazard Analysis | Comments
| 1 | Does the inspection task involve exposed energized conductors or circuit parts?
| 2 | Can the risk of exposure to electrical hazards be justified?
| 3 | What is the voltage of the equipment that requires inspection?
| 4 | Where are the approach boundaries for shock protection?
| 5 | Will the inspection involve crossing any of the approach boundaries?
| 6 | Has an incident energy analysis been performed for the equipment?
| 7 | Are the available short-circuit current and clearing times known?
| 8 | Where is the Arc Flash Boundary?
| 9 | Will any part of the body be within the Arc Flash Boundary?
| 10 | How will PPE(Personel protected equipment) for arc flash protection be selected?
| 11 | Is the appropriate arc-rated PPE available?
| 12 | Is the inspector qualified for this specific task and risk?

## Table 2
Checklist 2: General Requirements for Electrical Inspections
✔ | Item | Inspection Activity | Comments
| 1 | Identify installations or parts of installations that are covered by the NEC.
| 2 | Verify that installations have been made in accordance with the instructions included in listing and labeling of materials and equipment.
| 3 | Identify installations and equipment requiring special approval or investigation.
| 4 | Verify that interrupting ratings and short-circuit current ratings are adequate for the conditions of the installation.
| 5 | Verify that unused openings have been effectively closed.
| 6 | Check for broken or damaged parts and contamination by foreign materials.
| 7 | Check for secure mounting and adequate ventilation space for equipment.
| 8 | Check for proper use and ratings of splices and terminations.
| 9 | Check temperature ratings of terminations.
| 10 | Check for arc flash protection warning signs.
| 11 | Check for markings on enclosures and verify appropriate ratings for the environment.
| 12 | Verify adequate working clearances, dedicated spaces, and headroom around equipment.
| 13 | Verify that working space and dedicated space are not used for storage.
| 14 | Check adequacy of entrance to and egress from working space in general and verify that spaces containing large equipment have at least two entrances/exits or the equivalent.
| 15 | Verify that working spaces have adequate illumination.
| 16 | Check for identification of disconnecting means and circuit directories for panelboards, switchboards, switchgear and similar equipment.

## Table 3
Checklist 3: General Wiring Methods
✔ | Item | Inspection Activity | Comments
| 1 | Identify the wiring methods in use and verify their suitability for the occupancy and conditions.
| 2 | Verify that all conductors of a circuit are grouped together.
| 3 | Check insulation values where conductors of different systems share common enclosures.
| 4 | Check wiring methods for spacing from edges of framing and for protection from nails and screws.
| 5 | Check for insulating bushings or grommets where NM cable is installed through metal studs or where insulated conductors 4 AWG or larger enter enclosures.
| 6 | Check cover, fill, protection, and allowances for ground movement on underground conductors and raceways.
| 7 | Verify that electrical raceways and cable trays are used exclusively for electrical conductors.
| 8 | Check for continuity and completeness in metal raceways and enclosures.
| 9 | Verify that wiring methods are securely fastened in place, supported independently of suspended ceilings, and not used as supports.
| 10 | Check for continuity of grounded conductors in multiwire branch circuits.
| 11 | Check for adequate length of free conductors in boxes.
| 12 | Verify that boxes are installed at junction, splice, outlet, switch, and pull points.
| 13 | Check conductor fill in raceways.
| 14 | Verify that raceway systems are complete prior to installation of conductors.
| 15 | Check vertical raceways for adequate conductor supports.
| 16 | Verify that fire ratings have been restored at electrical penetrations.
| 17 | Check installations of wiring in ducts, plenums, and other air- handling spaces for proper methods and materials.
| 18 | Verify that access to equipment behind removable panels is not compromised by cables, raceways, or equipment.

## Table 4
Checklist 4: Switches and Receptacles
✔ | Item | Inspection Activity | Comments
| 1 | Verify that all switching is done in the ungrounded conductors.
| 2 | Verify that any switches in wet locations are properly installed in weatherproof enclosures.
| 3 | Verify that switches are located not over 6 ft 7 in. (2.0 m) high and that they can be operated from readily accessible places unless otherwise permitted.
| 4 | Verify that the voltage between adjacent grouped or ganged devices is not over 300 volts or that barriers are installed.
| 5 | Verify that metal switch boxes, switches, and any metal faceplates are grounded.
| 6 | Verify that switches or receptacles in boxes have their plaster ears seated against the wall surface or the box.
| 7 | Verify that switches and receptacles are used within their ratings.
| 8 | Verify that general-use dimmers are installed only for control of permanently installed incandescent lighting.
| 9 | Check the listing and marking of any switches or receptacles used with aluminum conductors.
| 10 | Check receptacles in wet or damp locations for proper covers and enclosures and weather-resistant ratings.
| 11 | Verify that isolated ground receptacles are properly identified and connected to isolated grounding conductors.
| 12 | Check that receptacles project from metal faceplates or are flush with nonmetallic faceplates and that the faceplates cover openings.
| 13 | Check receptacles for proper polarity and for grounding and bonding connections.
| 14 | Verify that receptacle ratings and branch-circuit ratings are compatible.

## Table 5
Checklist 5: Services
✔ | Item | Inspection Activity | Comments
| 1 | Verify that each building or structure has only one service or, if more than one, that additional services are justified and identified.
| 2 | Verify that each service drop or lateral supplies only one set of service-entrance conductors or, if more than one, that the additional sets are justified and identified.
| 3 | Check clearances from building openings, grade, roadway, roofs, and swimming pools.
| 4 | Verify that the point of attachment for an overhead service drop is adequate and will provide minimum clearances.
| 5 | Verify that masts used as supports for service-drop conductors have adequate strength and are not used to support other conductors or equipment.
| 6 | Verify that supports for service conductors passing over a roof are adequate and substantial.
| 7 | Check underground conductors for adequate burial depth and protection.
| 8 | Check above-ground conductors and cables for adequate supports and protection from physical damage.
| 9 | Verify that wiring methods and support systems for service- entrance conductors are suitable.
| 10 | Verify that service raceways are arranged to drain and that service heads are raintight and properly located.
| 11 | Check service conductors for adequate size and rating.
| 12 | Verify that service equipment is identified as suitable for that use.
| 13 | Verify that a service disconnecting means is provided, suitable, and located outside or inside nearest the point of entrance of the service conductors.
| 14 | Verify that service overcurrent protection is provided, properly sized, and part of or adjacent to the disconnecting means.
| 15 | Verify that service disconnects are grouped together and limited to six in any one location.
| 16 | Check ratings of service disconnecting means.
| 17 | Check for equipment connected to the supply side of the service disconnecting means and overcurrent protection.
| 18 | Verify that ground-fault protection is supplied where required, and obtain a written record of performance testing.

## Table 6
Checklist 6: Feeders
✔ | Item | Inspection Activity | Comments
| 1 | Verify that feeder conductors, including any required neutral conductors, are adequate for the load.
| 2 | Check overcurrent device and feeder conductor sizing for continuous and noncontinuous loads.
| 3 | Check wiring methods for suitability.
| 4 | Check feeders with disconnecting means rated at 1000 amperes or greater for ground-fault protection for equipment if required.
| 5 | Verify that disconnects are provided at separate structures for feeders running between structures.
| 6 | Verify that disconnects at separate structures are properly rated, located, grouped, and identified.
| 7 | Verify that any outside feeders use appropriate wiring methods and are properly supported and arranged to drain.
| 8 | Check any outside feeders for adequate supports, clearances, and mechanical protection.
| 9 | Verify that feeders supplied from transformers or from other feeders are properly protected by overcurrent devices.
| 10 | Check panelboards supplying or supplied by feeders for overcurrent protection, grounding, and proper enclosures.
| 11 | Verify that an identification scheme for ungrounded feeder conductors has been established and made readily available or posted where the premises wiring system has feeders that are supplied by more than one nominal voltage system.

## Table 7
Checklist 7: Branch Circuits
✔ | Item | Inspection Activity | Comments
| 1 | Verify that wiring methods used are appropriate for the conditions and occupancy.
| 2 | Check panelboards for proper overcurrent protection.
| 3 | Check individual and multioutlet branch circuits for proper ratings.
| 4 | Check conductors and overcurrent protection for consideration of continuous and noncontinuous loads, multioutlet loads, and minimum ampacity and size.
| 5 | Check branch circuits supplying receptacles and other outlet devices for permitted ratings of circuits and receptacles.
| 6 | Verify that branch-circuit loads do not exceed maximum permitted loads.
| 7 | Verify that branch circuits supplying motors are sized according to Article 430 or 440 and that inductive lighting loads are based on ballast ratings.
| 8 | Verify that branch circuits are used to supply only permissible loads based on their ratings.
| 9 | Verify that the number of branch circuits is adequate and that the load is evenly proportioned among the branch circuits.
| 10 | Check for compliance with branch-circuit voltage limitations.
| 11 | Verify that branch circuits for specific loads meet the requirements of the applicable articles.
| 12 | Check for proper use and identification of multiwire branch circuits.
| 13 | Check for required receptacles and lighting at mechanical equipment and service equipment.
| 14 | Check for required outlets or receptacles for show windows and signs.
| 15 | Verify that receptacles are provided for all cord-and-plug–connected appliances and where other flexible cords are used.
| 16 | Verify that GFCI protection is provided for receptacles in bathrooms, in kitchens, near sinks, outdoors, on rooftops, in indoor wet areas, in locker rooms with showers, and in garages.
| 17 | Verify that disconnects are provided at separate structures for branch circuits running between structures.
| 18 | Check for adequate size and clearances for outside branch circuits.
| 19 | Verify that an identification scheme for ungrounded branch-circuit conductors has been established and made readily available or posted where the premises wiring system has branch circuits that are supplied by more than one nominal voltage system.

## Table 8
Checklist 8: Service Grounding and Bonding
✔ | Item | Inspection Activity | Comments
| 1 | Determine what grounding electrodes are present on the premises.
| 2 | Determine which other electrodes are required or used.
| 3 | Verify that the grounding electrode conductor or conductors and bonding jumpers are properly sized.
| 4 | Verify that the grounding electrode conductors are protected and secured.
| 5 | Verify that grounding electrode conductor enclosures are properly bonded.
| 6 | Verify that the grounding electrode conductor is either unspliced or spliced using appropriate methods.
| 7 | Check for correct size and installation of any rod, pipe, or plate electrodes.
| 8 | Verify the accessibility of grounding electrode conductor connections.
| 9 | Check physically the soundness of bonding and earthing connection to every electrical equipment, structural steel, lightning arrestor etc. and inter-panel connections.
| 10 | Check if the terminations of the overhead shield wire covering the whole sub-station are in good physical condition and properly bonded electrically to the structures.
| 11 | Check condition of connections to the buried rails.
| 12 | Check for proper size and length of bonding jumpers around water meters and the like.
| 13 | Check the size, type, and installation of the main bonding jumper.
| 14 | Verify that service raceways and enclosures are correctly bonded.
| 15 | Check the size of service-equipment supply-side bonding jumpers.
| 16 | Verify that the grounded service conductor size is adequate.
| 17 | Verify that water pipe and structural metal building frames in the area served by each separately derived system are bonded.
| 18 | Verify that an intersystem bonding termination has been provided.
| 19 | Verify that where a wire-type EGC is also used as a grounding electrode conductor, it meets all applicable requirements for both grounding electrode conductors and EGCs.

## Table 9
Checklist 9: Equipment Grounding and Bonding
✔ | Item | Inspection Activity | Comments
| 1 | Identify equipment that is required to be grounded.
| 2 | Verify appropriate grounding methods for equipment fastened in place or connected by permanent wiring methods.
| 3 | Verify appropriate types of EGCs.
| 4 | Check separate EGCs for proper sizing and identification.
| 5 | Check connections of EGCs within outlet boxes.
| 6 | Verify that proper methods are used to bond receptacles to boxes.
| 7 | Record earth resistance to body of electrical equipment as well as to all parts of the fencing and structural steel work.
| 8 | Check installation of equipment bonding jumpers, especially where flexible connections or cords are used.
| 9 | Verify grounding of panelboard enclosures and connections of EGCs to panelboard metallic enclosures.
| 10 | Verify proper grounding at separate buildings or structures.
| 11 | Check equipment grounding of electric ranges and clothes dryers.
| 12 | Verify bonding of equipment operating at over 250 volts to ground.
| 13 | Check installations with isolated grounding conductors for proper connections and for grounding of the associated enclosures and wiring methods.
| 14 | Check for occupancies or equipment with special grounding or bonding requirements.

## Table 10
Checklist 10: Motors
✔ | Item | Inspection Activity | Comments
| 1 | Verify that ampacities and sizing of components other than overload devices are based on table values rather than on nameplate values.
| 2 | Verify that conductor ampacities for individual motors are at least 125 percent of table FLC.
| 3 | Check conductors supplying multiple motors or motors and other loads for ampacities equal to at least the sum of other motors or loads plus 125 percent of largest motor.
| 4 | Verify that motor overload protection does not exceed permitted values.
| 5 | Verify that short-circuit and ground-fault protection for motor branch circuits does not exceed permitted values.
| 6 | Verify that short-circuit and ground-fault protection for motor feeders does not exceed permitted values.
| 7 | Check motor control circuits for proper overcurrent protection.
| 8 | Verify that motor controllers are provided for motors and that they are of the proper type and have adequate ratings, including short-circuit current ratings.
| 9 | Check MCCs for proper ratings, protection, workspace, and dedicated space.
| 10 | Verify that motor disconnects are of the proper type and rating.
| 11 | Verify that controller disconnects are in sight of controllers, are readily accessible, and have adequate workspace.
| 12 | Verify that motor disconnects are in sight of motors, are readily accessible, and have adequate workspace.

## Table 11
Checklist 11: Air-Conditioning and Refrigerating Equipment
✔ | Item | Inspection Activity | Comments
| 1 | Identify equipment subject to Article 440—Equipment Containing Hermetic Refrigerant Motor-Compressor(s).
| 2 | Identify the applicable nameplate information for the equipment.
| 3 | Verify that branch-circuit conductor sizes are adequate on the basis of the applicable nameplate information.
| 4 | Verify that conductors supplying several units are adequately sized.
| 5 | Verify that branch-circuit overload protection is provided and properly sized.
| 6 | Verify that branch-circuit short-circuit and ground-fault protection is provided and properly sized.
| 7 | Verify that feeder short-circuit and ground-fault protection is provided and properly sized where applicable.
| 8 | Verify that controllers have adequate ratings, including short-circuit current ratings, where they are not part of listed multimotor or combination-load equipment.
| 9 | Verify that disconnecting means have ratings adequate for the equipment.
| 10 | Verify that the disconnecting means are within sight and readily accessible from the equipment and that working spaces are adequate.
| 11 | Verify that conductors, receptacles, cords, and overcurrent devices for room air conditioners are properly sized and that LCDI devices or AFCI protection is provided for cords.
| 12 | Check for receptacles and adequate lighting for servicing of mechanical equipment.

## Table 12
Checklist 12: Transformers
✔ | Item | Inspection Activity | Comments
| 1 | Identify transformers that are covered by Article 450.
| 2 | Verify that overcurrent protection for transformers over 1000 volts is provided and properly sized.
| 3 | Verify that overcurrent protection for transformers 1000 volts or less is provided and properly sized.
| 4 | Verify that overcurrent protection is provided for transformer primary conductors.
| 5 | Verify that overcurrent protection is provided for transformer secondary conductors.
| 6 | Check transformer installations for adequate ventilation and spacing from walls and obstructions.
| 7 | Check transformers for ready access or proper installation in the open or in hollow spaces.
| 8 | Verify that transformers are supplied with a disconnecting means.
| 9 | Check indoor dry-type transformers for separation from combustibles or, based on ratings, installation in fire-resistant rooms or vaults.
| 10 | Check outdoor dry-type transformers for weatherproof enclosures.
| 11 | Verify that liquid-insulated transformers are installed in accordance with the requirements for the location and type of insulating liquid.
| 12 | Check transformer vaults for adequate construction, access, ventilation, and drainage and for foreign systems in vaults.
| 13 | Check silica-gel breather. If turning pink in appearance, replace it with dry gel (blue colour) and recondition the old silica gel. If the silica gel is too wet, check dielectric strength of transformer. oil.
| 14 | Check for oil leakage on transformer body, conservator tank, oil drain valve and foundations. If leaking, take corrective action by tightening the bolts; replace gaskets, if necessary.
Potential & Current Transformers
✔ | Item | Inspection Activity | Comments
| 1 | Clean the Insulator or bushing with dry cotton cloth. Check for any flash, crack or chipping. Anti track paint should be applied on the chipping flash marks.
| 2 | Check tightness of all nut and bolts of busbar connector and secondary terminals.
| 3 | Check earthing connections for tightness.
| 4 | Check PT fuse for healthiness.
| 5 | Check bimetallic strip in CT for any sulphation, replace if required.

## Table 13
Checklist 13: Motorised & Manual Isolators
✔ | Item | Inspection Activity | Comments
| 1 | Check the electrical interlocking between circuit breaker and associated isolators both locally and remotely.
| 2 | Check all wiring connections, nuts and bolts for any looseness and tighten if required.
| 3 | Check the clearance between male and female blades in open condition it should be ≥ 50 cm for vertical brake isolators.
| 4 | Check the pedestal insulator for any chipping and dust. Clean with dry cotton cloth. In case of chipping apply anti track paint.
| 5 | Grease the main bearing in control box through grease nipple. The other rotating parts should be lubricated using mobil oil.

## Table 14
Checklist 14: Overhead Equipment
✔ | Item | Inspection Activity | Comments
| 1 | Visually inspect every part of Flexible OHE (including feeder line) so that any defect and abnormalities noticed are recorded and reported to the maintenance team.
| 2 | With OHE Inspection Car running on main line, check if pantograph glides smoothly under the main line OHE without any contact to OHE of loop line.
| 3 | Check for any chipped or damaged insulators or displaced fittings.
| 4 | Check for any excessive sagging or hogging of contact wire.
| 5 | Verify the presence of protective screens, caution and warning boards and anti-cllimbing devices.
| 6 | Check and remove bird nests, obstructions including branches of trees, and pieces of stray wire likely to cause short circuits
| 7 | Check carefully condition of contact and Catenary wires, particularly for kinks and twists in contact wire and broken strands of Catenary wire
| 8 | Check all steel parts and remove rust, if any, and paint them.
| 9 | Check all anchors for tightness of bolts, nuts, check nuts and pins, Lubricate all turn buckles/adjusters and pulleys
| 10 | Check verticality of all masts with plumb bob and take remedial action as required.

## Table 15
Checklist 15: Battery Bank & Battery Chargers
✔ | Item | Inspection Activity | Comments
| 1 | Clean the accumulated dust using paint brush & dry cotton cloth over cell terminals, vent plug and cell body, starting from top to bottom row of cells
| 2 | Check all the battery inter-cell links, cable connector and earthing connections for tightness. Replace with New/Overhauled links if sulphation is found.
| 3 | Check electrolyte level - should be between Max-Min marks. Top up with distilled water if required.
| 4 | Check battery bank stand for any rusting, paint if required
| 5 | Check each cell for leakage and bulging. If found, replace with new cell
| 6 | Observe the charger for any abnormal sound. Rectify the same if found.
| 7 | Check working of automatic changeover of the charger.
| 8 | Check working of alarm, indications, switches (Input, output, auto/manual, and float/boost) ammeter and voltmeter at charger as well as in SCADA.
| 9 | Switch OFF the charger, open the cover and clean accumulated dust with vacuum cleaner.
| 10 | Check all cables (AC I/P & DC O/P) & earthing connection for tightness.
| 11 | Check the PCB card and multi pin connector for any damage/heating mark. Clean PCB cards with soft hair brush.

## Table 16
Checklist 16: Circuit Breakers |  |  |  | Checklist: VCB & SF6 Circuit Breakers
✔ | Item | Inspection Activity | Comments | ✔ | Item | Inspection Activity | Comments
| 1 | Open the cover of control box. Examine the interior and remove the accumulated dust, if any part of the interior is badly rusted indicating entry of moisture, find out the cause, plug the holes and repaint the rusted parts. |  |  | 1 | Open the cover of control box. Clean the accumulated dust by vacuum cleaner. Also clean the sight glass.
| 2 | Check in particular if the weatherproof gaskets are in good condition; if not, replace them to make the control box watertight and dust-tight |  |  | 2 | Check the operation manually as well as electrically in local and remote mode, observe whether the mechanism functions smoothly without any rubbing or obstruction.
| 3 | Examine if the leading in pipe connections are properly bushed, sealed and watertight. Check if all pins and check-nuts are in place. Check also tie-rod nuts for tightness. |  |  | 3 | Check working of semaphore indicator for open/close mechanism.
| 4 | Examine the commutator of the motor and clean with muslin cloth. Examine carbon brushes and replace if necessary. |  |  | 4 | Verify from SCADA status, the change of position of local remote switch & open/close status.
| 5 | Check breather and breather holes for clogging.
| 6 | Check gear-oil level in the mechanism and replenish it, if required
| 7 | Check interlocks of the equipment and associated isolators.
| 8 | Verify from SCADA status, the change of position of local remote switch & open/close status.
Checklist: Interrupters
✔ | Item | Inspection Activity | Comments
| 1 | All Nuts, Bolts , Fasteners & Connections to be checked & tightened
| 2 | Operate isolator several times and observe if it operates smoothly and correctly. Check interlocks and integral lock, lubricate moving parts as necessary with appropriate lubricant.
| 3 | Check commutator of motor and clean with dry mull cloth, and check carbon brushes for proper bedding and wear. Check if motor is working smoothly, clean limit-switch and auxiliary switch contacts and check tightness of wiring connections. Examine contactor box and signal box; clean thoroughly and lubricate all gears, shafts, bearings contact etc.
| 4 | Clean all articulated joints, sliding and bearing surfaces thoroughly.

## Table 17
Checklist 17: Capacitors
✔ | Item | Inspection Activity | Comments
| 1 | Check capacitors for proper enclosures and guards.
| 2 | Verify that conductors are properly sized on the basis of the current rating of the capacitor(s).
| 3 | Verify that capacitors other than those connected to the load side of motor overload devices have disconnects and proper overcurrent protection.
| 4 | Verify that overload device ratings have been corrected where capacitors are connected to the load side of motor overload devices.
| 5 | Check capacitors over 1000 volts for proper switching, overcurrent protection, identification, and grounding.
| 6 | Verify that a proper means for discharge has been provided for capacitors.

## Table 18
Checklist 18: Emergency Systems
✔ | Item | Inspection Activity | Comments
| 1 | Determine the applicability of Article 700.
| 2 | Check equipment for suitability for approval.
| 3 | Review load calculations and verify that system capacity is adequate.
| 4 | Verify that system capacity is adequate for any nonemergency loads it feeds or that automatic selective load pickup and load shedding are provided.
| 5 | Verify that power sources are suitable and capable of supplying the load within 10 seconds and maintaining the load for at least 1½ hours.
| 6 | Verify that generators or fuel cells, if used, have on-site fuel adequate for at least 2 hours of operation and that fuel pumps, if any, are supplied by emergency power.
| 7 | Verify that unit equipment, if used, is fixed in place and connected to the same circuit that supplies normal lighting to the area, ahead of any local switches.
| 8 | Verify that transfer equipment is automatic, listed for emergency use, equipped with means for bypass, electrically operated, and mechanically held.
| 9 | Verify that transfer equipment supplies only emergency loads.
| 10 | Verify that audible and visual signals are provided as required. (Automatic disconnection of emergency systems on ground faults is not required.)
| 11 | Check for signs at service equipment indicating emergency system type and location and for signs at grounding locations indicating sources connected.
| 12 | Check boxes and enclosures for permanent identification as components of the emergency system.
| 13 | Verify that emergency wiring is entirely independent of other wiring, except as specifically permitted for common enclosures, luminaires, and boxes.
| 14 | Verify that emergency feeder circuits and equipment in high-rise (over 75 ft) buildings and assembly occupancies of over 1000 persons have suitable fire protection.
| 15 | Verify that emergency branch circuits supply only emergency loads.
| 16 | Verify that power to emergency lighting in areas served by high- intensity discharge (HID) luminaires is maintained until normal illumination is restored.
| 17 | Verify that emergency lighting equipment is arranged so that an area will not be left in total darkness by the failure of a single lighting element.
| 18 | Verify that emergency lighting is supplied automatically on failure of the normal power supply.
| 19 | Verify that any switches that may disconnect power to emergency lighting are conveniently accessible, but only to authorized persons.
| 20 | Verify that branch-circuit overcurrent devices in emergency circuits are accessible only to authorized persons.
| 21 | Verify that all emergency system overcurrent devices are selectively coordinated.
| 22 | Verify that surge protection is provided on emergency system switchboards and panelboards.
| 23 | Verify and witness that testing is conducted as required and that a written schedule and record for periodic testing and maintenance are provided.
| 24 | Check for compliance with NFPA 101, NFPA 110, and other applicable building codes.

## Table 19
Checklist 19: Legally Required Standby Systems
✔ | Item | Inspection Activity | Comments
| 1 | Determine the applicability of Article 701.
| 2 | Check equipment for suitability for approval.
| 3 | Review load calculations and verify that system capacity is adequate.
| 4 | Verify that system capacity is adequate for any optional standby loads it feeds or that automatic selective load pickup and load shedding are provided.
| 5 | Verify that power sources are suitable and capable of supplying the load within 60 seconds or less and maintaining the load for at least 1½ hours.
| 6 | Verify that generators, if used, have on-site fuel adequate for at least 2 hours of operation.
| 7 | Verify that unit equipment, if used, is fixed in place and connected to the same circuit that supplies normal lighting to the area, ahead of any local switches.
| 8 | Verify that transfer equipment is automatic, listed for emergency use, equipped with means for bypass, electrically operated, and mechanically held.
| 9 | Verify that audible and visual signals are provided as required. (GFP of equipment on legally required standby systems is not required.)
| 10 | Check for signs at service equipment indicating standby system type and location and for signs at grounding locations indicating sources connected.
| 11 | Check wiring for compliance with the general requirements of Chapters 1 through 4 of the NEC. (Separation of standby wiring from other general wiring is not required.)
| 12 | Verify that overcurrent protection devices for legally required standby systems are accessible to authorized persons only.
| 13 | Verify that all legally required standby system overcurrent devices are selectively coordinated.
| 14 | Verify and witness that testing is conducted as required and that a written schedule and record for periodic testing and maintenance are provided.

## Table 20
Checklist 20: Fire Alarm Systems
✔ | Item | Inspection Activity | Comments
| 1 | Verify that tubing, piping or other mechanical system is not installed in raceways and cable trays containing conductors for Class 1, Class 2, and Class 3 circuits.
| 2 | Verify that installation of cables does not prevent access through panels designed to provide access.
| 3 | Verify that cables have been supported to prevent damage under normal conditions.
| 4 | Check on proper identification of fire alarm circuits at junction and terminal locations.
| 5 | Distinguish nonpower-limited from power-limited fire alarm circuits and verify power supply is supplied by a branch circuit that supplies only loads associated with the fire alarm system and is not protected by GFCI or AFCI devices.
| 6 | Verify overcurrent protection for 18 and 16 AWG nonpower-limited fire alarm circuit conductors.
| 7 | Check for proper nonpower-limited wiring methods.
| 8 | Check insulation type and rating of nonpower-limited circuit conductors.
| 9 | Verify proper raceway fill and derating for nonpower-limited circuits.
| 10 | Verify proper application of listed nonpower-limited fire alarm cables.
| 11 | Verify listing of power-limited source and that the power supply is supplied by a branch circuit that supplies only loads associated with the fire alarm system and is not protected by GFCI or AFCI devices.
| 12 | Check equipment marking to indicate power-limited circuit.
| 13 | Verify proper wiring methods on the load side and supply side of a power-limited source.
| 14 | Verify separation of power-limited fire alarm circuits from other circuits.
| 15 | Verify that power-limited fire alarm circuits are not supported from raceways.
| 16 | Verify proper application of listed power-limited fire alarm cables.
| 17 | Check listing and marking of listed power-limited fire alarm cables.